339 Motor Protection System

Guideform Specification

August 2010

The motor protection relay shall provide primary protection for medium voltage motors.   The relay shall be equipped with the following protection functions.

Motor Thermal Overload Model (49)

  - Include 15 standard overload curves to account for various motor types and applications.

  - The stator protective thermal model shall combine inputs from phase and unbalance currents, and RTD winding feedback. This will then cause the model to become dynamic in nature in order to follow the loading and temperature of the motor.

  - Motor cooling time constants

  - Rotor protection during stall and acceleration.

The relay shall detect ground faults or earth leakage currents as low as 0.50 A using a 50:0.025 Ground CT.

Use phase and unbalance current heating to calculate motor thermal capacity during starting and running states

Settable motor stopped and motor running cooling time constants

Phase Undervoltage (27P)

Load-loss (undercurrent) / Underpower (37)

Bearing RTD (38)

Unbalance / single phase protection (46)

Voltage Phase Reversal (47)

Incomplete Sequence (48)

Phase and Ground Instantaneous overcurrent elements (50P/50G)

Neutral Instantaneous overcurrent element (50N)

Breaker Failure / Welded Contactor (50BF)

Load Increase / Mechanical Jam / Locked Rotor (51R)

Phase Overvoltage (59P)

Negative Sequence Overvoltage (59_2)

Starts-per-hour (66)

Over Frequency (81O)

Under Frequency (81U)

VT Fuse Failure (VTFF)

Motor stall protection

Re-start blocking timer to be used as a start permissive to ensure the motor had slowed to a safe speed or to a complete stop, before it can be re-started again

Minimum-time-between-starts

The Motor Protection relay shall accept 12 RTD inputs via a remote RTD module.

The RTD module shall communicate to the Motor Protection Device via a CANBUS interface.

The remote RTD device shall be fully configurable via the Motor Protection Device.

Remote RTD inputs with associated over-temperature protection functions including alarm and trip settings.  The following additional functionality shall be provided, associated to RTDs:

  - Able to configure each of the RTDs as “None” or any one of four application types: “Stator”, “Bearing”, “Ambient”, or “Other”

  - RTD type shall be 100 Ohm Platinum

  - The motor relay shall incorporate the RTD inputs to support the following:

    - Thermal overload model biasing

    - Temperature alarms and trips (49RTD/38)

    - RTD open- or short-circuit alarm

  - The motor relay shall include trip voting for extra reliability in the event of RTD malfunction.  If enabled, a second RTD must also exceed the trip temperature of the RTD being checked before a trip is issued

  - Provisions shall be included to allow the RTDs to be identified by name

The relay shall be able to monitor one remote RTD module.  The remote RTD module each with 12 RTD inputs, with associated over-temperature protection functions including alarm and trip settings.

The relay shall have a draw-out construction to facilitate testing, maintenance and interchangeability.  The relay shall have a set-screw on the draw-out handle.

The relay shall be equipped with an ambient temperature monitor that continuously monitors the temperature that the relay is exposed to.  The ambient temperature monitor shall alarm when the device is exposed to extreme temperatures and undesirable conditions such as air-conditioning unit or station heater failures.

The motor protection relay shall have seven (7) output relays.

- 2 Form-A with coil monitor

- 5 Form-C

The motor protection relays shall have ten (10) digital inputs.  The digital inputs shall be fully user programmable and have four voltage thresholds.

The relay shall provide complete monitoring and metering functions. These shall include:

Current: Phasors, RMS Values of per Phase, Average, Motor Load, Current Unbalance, Unbalance Biased Motor Load, Ground

Voltage: Phase-to-Phase and Phase-to-Ground

Power: Active, Reactive, Apparent and Power Factor

Frequency

Temperature of each RTD Input from the RMIO unit

An event recorder with a record of the last 256 events, time tagged with a resolution of 1ms.

The waveform capture (oscillography) feature is similar to a transient/fault recorder. The oscillography shall capture 32 samples per cycle and the digital states.

The relay shall be able to provide data in the form of trending or data logger, sampling and recording up to ten actual values at an interval defined by the user.  Several parameters shall be trended and graphed at sampling periods. The parameters for the data logger will be captured by the motor protection relay and shall be:  Phase Currents A, B, and C, and Average Phase Current, Motor Load, Current Unbalance, Ground Current, Hottest Stator RTD, Thermal Capacity Used and  RTDs 1 through 12 that are connected to the RMIO unit.

Start block timer status including overload lockout, start inhibit, starts per hour, time between starts, and restart block

The relay shall have starter failure detection feature which shall produce an alarm in the event that the motor relay does not detect a starter/breaker open condition after a trip is initiated.

Security / Change History Report

The relay must comply with NERC CIP security reporting requirements and provide traceability.  The relay must maintain a history of the last changes made to the configuration, including modifications to settings and firmware upgrades.  A summary history of the last ten sessions and a list the last 100 specific setting changes made must be recorded and stored in non-volatile memory.  The report must be available to be saved and printed in PDF format.

Security Setting Reports must have the following information:

- Dates and times of setting changes

- MAC address of user making setting changes

- Listing of modified changes

- How setting changes were made

  - Keypad, Front USB port, Ethernet & Rear serial port

User interfaces shall include:

A 4 x 20 character LCD display, and navigation keys

Indicator LEDs on the front panel which shall provide a quick visual indication of status

A front panel USB serial port that shall provide easy computer access. The communications protocol shall be Modbus RTU

One rear RS485 port. The communications protocol shall support Modbus RTU

An optional RJ45 and MTRJ Fiber Optic Ethernet port shall be provided to allow 10BaseT Ethernet connectivity to Local or Wide Area Networks.  The communications protocol shall be Modbus TCP

The relay shall support the following communication protocols:

  - Modbus RTU

  - Modbus TCP/IP

  - IEC 61850 GOOSE

  - IEC 61850 Logical Nodes

  - DNP 3.0

  - IEC 60870-5-104

  - IEC 60870-5-103

The Motor Protection Relay shall have an IRIG-B input to allow time synchronization using a GPS clock over a wide area network.

The IRIG-B input shall support both AM and DC time synchronization with an auto detect feature that removes the requirement of manual selection.

The relay shall be capable of being set by Windows-based, Easy to use, Setup graphical terminal interface

To make the data acquisition more efficient, the motor relay shall provide a User Definable Memory Map, which shall allow a remote computer to read up to 125 nonconsecutive data registers by using one Modbus packet.  The User Definable Memory Map shall be programmed to join any memory map address to one in the block of consecutive User Map locations, so that they can be accessed by means of these consecutive locations. The User Definable area shall have two sections:

  - A Register Index area containing 125 Actual Values registers

  - A Register area containing the data located at the addresses in the Register Index

The relay must be capable of being programmed through a windows based software program that is capable of the following:

- The software program will operate in the following fashion

  - Request system and motor nameplate data from user through display screens.

  - Generate settings file

  - Review settings with user with the option to disable any configured settings that are not required

  - Provide PDF report outlining the settings that have been generated

  - Report and Settings file to be saved in user-selectable location

- The setup software shall allow the user to program the relay via a ‘Quick Setup’ feature.

- The following system and protection settings will be generated based on inputted information

  - All CT System settings

  - All Thermal Model settings including

    - Short Circuit

    - Mechanical Jam

    - Unbalance

    - Undercurrent

    - Ground Fault

  - All Motor Start / Inhibit protections

  - Remote RTD configuration, alarming and tripping

- Provide a summary of all enabled settings in a PDF format that can be saved or printed.

Automation

- The Motor Protection Relay shall have programmable automation functions to allow the user to build simple logic.

  - The logic must include 16 (sixteen) logic elements

  - The logic elements can be programmable using the state of any contact, virtual or remote input or an output operand from protection or control elements.

  - The logic provides for assigning up to three triggering inputs in a ‘AND/OR’ gate for the logic element operation and up to three blocking inputs in an ‘AND/OR’ gate for defining a block signal.

  - Pickup and dropout timers shall be available for delaying the logic element operation and reset respectively.

Motor Health Report

The Motor Health Report included with the relay will provide a detailed history of the operation and performance of the associated motor in both graphical and data format.  The following information will be provided in the Motor Health Report.  The report can either be saved to a location in a soft copy or be printed in PDF format.

The report shall be divided into seven categories and provide the following information:

- Device Summary

  - Requested Period

  - Report Created By

  - Motor Name

  - Protection Device

  - Firmware Version

  - Motor FLA

  - Rated Voltage

  - Phase Rotation

  - System Frequency

  - Motor Running Time

- Status Overview

  - Provide historical learned data of the following

  - Acceleration Time

  - Starting Current

  - Starting Capacity

  - Motor Load

  - Run Time After Start

- Trip Summary

  - Overload / Thermal

  - Current

  - Miscellaneous

  - Information shall be represented both graphically and numerically

- Motor Operating History

  - The Motor Operating History will provide information extracted from the Events Record

  - Motor Start / Running

  - Manual Stop Command

  - Trip Command

  - Lockout

  - Alarm Conditions

  - Emergency Restarts

  - Information shall be represented both graphically and numerically

- Motor Starting Learned Information

  - Learned Data will be captured for every motor start

  - 250 Learned Data Records will be stored in the relay

  - Learned Acceleration Time

  - Learned Starting Current

  - Learned Starting Capacity

  - Learned Average Motor Load

  - Learned Average Run Time After Start

  - Information shall be represented both graphically and numerically

- Motor Start Data Logger

  - The Motor Start Data Logger consists of Baseline Record and 5 additional records

  - Each record shall contain 10 channels of information

  - Each channel shall contain 150 samples, sampled at 200ms intervals for a total of 30 seconds

  - Information to be included in the Motor Start Data Logger:

  - Average Current

  - Average Current Unbalance in Percent

  - Ground Current

  - Thermal Capacity Used

  - Breaker Status

  - Information shall be represented both graphically and numerically

- Motor Stopping / Tripping

  - Events that are related to the stopping or tripping of the motor

  - Overload Trip

  - Mechanical Jam

  - Short Circuit

  - Current Unbalance

  - RTD Temperature

  - Ground Fault

  - Manual/Remote Stop

  - Information shall be represented both graphically and numerically

To help extend product life, and to protect the motor protection relay from hostile and harsh environments including moisture, temperature variations, salt spray, organic attack (fungus), and aggressive chemicals and vapors, the product manufacturer shall provide optional harsh environment conformal coating.

For more information on this product visit the GE Multilin Web Site from a product brochure at:

http://www.gedigitalenergy.com/multilin/catalog/339.htm