B30 Guideform Specifications  (Firmware revision 5.20)

Restrained and unrestrained (instantaneous) low-impedance bus differential protection with enhanced immunity to CT saturation shall be provided in one integrated package suitable for incorporation in an integrated substation control system. The relay shall be applicable to busbars of a maximum of six circuits.

# Protection functions:

## Restrained Bus Differential

The element shall use two voltage-independent protection principles, current differential and phase comparison, with additional CT saturation detection.

The differential principle shall be based on dual-slope dual-breakpoint characteristic with the maximum zone current used for restraint.

The phase comparison principle shall check directional relation between the relevant zone currents to differentiate between internal and external faults. Selection of the currents for comparison shall be adaptive.

The CT saturation detection mechanism shall distinguish between internal and external faults having as little as one-eighth of a power system cycle of undistorted current waveforms.

Automatic CT ratio compensation shall be included.

The differential element shall be selectable as restrained or Unrestrained Differential

## Overcurrent Protection

Multiple time overcurrent elements: for phase, neutral, and ground currents shall be provided.

Time overcurrent curve characteristics: IEEE, IEC, IAC, I2t, definite time, and four custom curves for precise or difficult coordination shall be available.

Phase Instantaneous Overcurrent protection shall be available.

## Voltage Protection

One phase undervoltage element shall be provided per each relay voltage input.

One neutral overvoltage element shall be provided per each relay voltage input.

# Monitoring functions:

## CT Trouble

The element shall respond to differential current and when used in conjunction with voltage supervision shall provide desired response to CT fail conditions.

## Dynamic bus replica

The relay shall allow to associate a dynamic connection status signal with each input to the differential element in order to dynamically include or exclude a given current from the differential calculations.

The status signal could be any user flag available in the relay, especially position of any input contact or a combination of thereof via programmable logic. Isolator contact discrepancy alarming shall be available via programmable logic.

# Control functions:

The relay shall have user programmable logic including non-volatile latches

Sixteen user-definable protection functions

Flexible control of all input and output contacts shall be provided.

All elements shall have a blocking input that allows supervision of the element from other elements, contact inputs, etc.

The relay shall allow for peer-to-peer communications using direct fiber or G.703 or RS422 interfaces.

The relay shall have switchable setting groups for dynamic reconfiguration of the protection elements due to changed conditions such as system configuration changes, or seasonal requirements.

# Metering Functions:

The relay shall provide metering values of voltage (phasors, true RMS values, symmetrical components), current (phasors, symmetrical components, true RMS values), and frequency.

Differential and restraint currents shall be available in terms of magnitude and angle for easy testing, commissioning and troubleshooting.

# Digital Fault Recorder (DFR)

- The relay shall provide the following disturbance recording capability.

  - Oscillography (Transient Recorder): The relay shall have the capability to store raw sampled data with programmable sampling rate (max of 64 samples per cycle) with a provision for 64 records to store/monitor information about any physical I/O point or internal digital and analog quantities.

  - Sequence of Event recorder (SOE) function with a capacity to store 1024 events with 1ms time stamping accuracy.

# Relay HMI

- The relay shall provide the following user interface capabilities.

  - Provisions for 48 user programmable LEDs and custom labeling capabilities

  - Provisions for 12 large user programmable pushbuttons to perform manual control, operate breakers, or lock-out functions and its operation shall be logged directly in the sequence of events recorder.

# Communications

- The relay shall provide different networking options including Ethernet-fiber with optional redundancy and RS485 interfaces.

- The relay shall support protocols DNP3.0, Modbus RTU, Modbus TCP/IP and IEC60870-5-104 with the option of IEC61850 protocol.

- The relay shall also provide exchange of binary information between other UR devices over a dedicated multimode fiber, RS422, G.703 or IEEEC37.94 interface.

- The relay clock shall be capable of being synchronized with an IRIG-B signal to allow synchronism with other connected devices. The relay shall allow for SNTP network-based time synchronization.

# General Requirements

The contact inputs shall accept wet or dry contacts. Contact outputs shall be trip rated Form-A with current and voltage circuit monitors, Form-C, or Fast Form-C for signaling. Hardware input/output capability shall be expandable.

The relay shall be supplied with supporting application software for use on a PC with Windows® operating systems. The program shall be capable of retrieving COMTRADE oscillography files from the relay to display, save, or print when troubleshooting. The software shall provide the capability of editing and managing settings files to store to the relay or disk backup, while on-line or off-line. The software shall also permit the updating of new relay firmware and viewing of all trip and alarm target messages, and the 1024 time stamped events recorded by the relay

Preference:

Manufacturer: GE Multilin

Device Number and Name: B30, Bus protection system