C60 Guideform Specifications

Firmware revision 3.00

Breaker protection, control, monitoring and metering shall be supplied in one integrated digital relay package for application on high voltage breakers, in single breaker or breaker-and-a-half applications, and suitable for incorporation into an integrated substation control system.

# Protection functions:

## Overcurrent Protection

Two time overcurrent elements per each current input of the relay: for phase and neutral, shall be provided.

Time overcurrent curve characteristics: IEEE, IEC, IAC, I2t, definite time, and four custom curves for precise or difficult coordination shall be available.

Two instantaneous overcurrent elements per each current input of the relay: for phase and neutral, shall be available.

## Voltage Protection

Two phase under- and one over-voltage elements per each voltage input of the relay shall be provided.

One auxiliary under- and over-voltage element shall be provided per each voltage input of the relay.

One neutral overvoltage (3Vo) element shall be provided per each voltage input of the relay.

The voltage element operating time shall be user adjustable.

## Sensitive Directional Power

Two elements shall be included each consisting of two stages.

The element characteristic angle shall be adjustable.

## VT Fuse Fail Detection

## Disturbance Detection

# Control Functions:

## Two Breaker Failure Elements

The breaker fail elements shall be configurable to respond to two different currents such as in breaker-and-a-half application.

The breaker fail elements shall respond to three levels of current in three-pole and single-pole modes as well as to breaker contacts.

## Two Synchrocheck Elements

The synchrocheck elements shall be configurable to respond to any combination of single-phase voltages such as in breaker-and-a-half application.

Dead source logic shall be included.

## Automatic Recloser

Four shot, three-pole/single-pole dual-breaker autorecloser shall be provided.

The autorecloser shall allow one breaker to be out of service while the other breaker is in service.

The autorecloser shall allow simultaneous or sequential reclosing of the two breakers.

The autorecloser shall allow applying different dead-times for single-line-to-ground and multi-phase faults. This shall include a single-line-to-ground fault evolving into a multi-phase fault.

## Breaker control feature for manual control of one or two breakers

## Two breaker arcing current features for predictive maintenance

## Eight FlexElements™ for user-definable protection functions

Flexible control of all input and output contacts shall be provided.

All elements shall have a blocking input that allows supervision of the element from other elements, contact inputs, etc.

The relay shall allow for peer-to-peer communications direct fiber or G.703 or RS422 interfaces.

## Switchable Setting Groups

The relay shall have switchable setting groups for dynamic reconfiguration of the protection elements due to changed conditions such as system configuration changes, or seasonal requirements.

# Monitoring and Metering Functions:

## Fault location and reporting

## Metering

- Voltage (phasors, true RMS values, symmetrical components), current (phasors, symmetrical components, true RMS values), real, reactive and apparent power, power factor, energy, demand and frequency.

## Breaker Arcing Current (I2t)

The relay shall calculate an estimate of the per phase wear on the breaker contacts by measuring and integrating the current squared passing through the breaker contact as an arc.

## User-programmable oscillography

## User-programmable Data Logger

## Trip circuit monitoring

UR Common Guideform Specifications

Firmware revision 3.00

The relay shall be provided in one integrated package suitable for incorporation in an integrated substation control system. The relay shall be housed in a horizontal, 4 RU, 19-inch rack chassis configuration. It shall be a modular design to easily facilitate upgrading or repair by replacement of modules. The faceplate interface shall include an alphanumeric vacuum fluorescent display, keypad, and LED target indicators.

The logic that determines the interaction of inputs, features, and outputs shall be re-configurable through the use of FlexLogic™ equations. The use of remote inputs and outputs in addition to hardware shall be available on the communications ports using the UCA2 GOOSE (Generic Object Oriented Substation Event) mechanism to minimize the requirement for auxiliary components and wiring. The contact inputs shall accept wet or dry contacts. Contact outputs shall be trip rated Form-A with current and voltage circuit monitors, Form-C, or Fast Form-C for signaling. Hardware input/output capability shall be expandable.

The relay shall have three communications ports that operate independently and simultaneously. The RS232 port shall be accessible from the faceplate of the relay. The second port shall be RS485 supporting ModBus® RTU and DNP 3.0 protocols capable of baud rates up to 115 kbps. The third communications port shall be either a similar RS485 port or a 10 Mbps Ethernet port supporting MMS/UCA2, ModBus®/TCP, and DNP 3.0 or IEC 60870 protocols. The physical port shall be 10BaseF, or redundant 10BaseF.

The relay shall be supplied with supporting application software for use on a PC with Windows® 95/98/NT operating systems. The program shall be capable of retrieving Comtrade oscillography files from the relay to display, save, or print when troubleshooting. The software shall provide the capability of editing and managing settings files to store to the relay or disk backup, while on-line or off-line. The software shall also permit the updating of new relay firmware and viewing of all trip and alarm target messages, and the 1024 time stamped events recorded by the relay.

The relay clock shall be capable of being synchronized with an IRIG-B signal to allow synchronism with other connected devices. The relay shall allow for SNTP network-based time synchronization.