B90 Guideform Specifications

Firmware rev.3.00

Low-impedance bus differential protection with enhanced immunity to CT saturation shall be provided in one integrated package suitable for incorporation in an integrated substation control system. The relay shall be applicable for single-busbars, double-busbars, triple-busbars with or without a transfer bus, meshed corners and breaker-and-a-half arrangements of a total of up to 24 current inputs.

The B90 has the following architecture:

Phase-segregated low-impedance solution shall be provided.

The scheme shall be configured using several separate UR IEDs.

Inter-IED communications shall be provided by means of dual-ring direct fiber connection.

Each IED shall accept a common setting file format.

Each IED shall be accessed simultaneously from the same PC configuration program.

The scheme shall allow for flexible distribution of digital inputs and output contacts between the IEDs.

# Protection Functions

## Restrained Bus Differential

The element shall use two voltage-independent protection principles, current differential and phase comparison, with additional CT saturation detection.

The differential principle shall be based on dual-slope dual-breakpoint characteristic with the maximum zone current used for restraint.

The phase comparison principle shall check directional relation between the relevant zone currents to differentiate between internal and external faults. Selection of the currents for comparison shall be adaptive.

The CT saturation detection mechanism shall distinguish between internal and external faults having as little as one-eighth of a power system cycle of undistorted current waveforms.

Automatic CT ratio compensation shall be included.

## Unrestrained Bus Differential

## Overcurrent Protection

One time overcurrent element shall be provided per each current input of the relay.

Time overcurrent curve characteristics: IEEE, IEC, IAC, I2t, definite time, and four custom curves for precise or difficult coordination shall be available.

One instantaneous overcurrent element shall be available per each current input of the relay.

## Voltage Protection

One undervoltage element shall be provided per each voltage input of the relay.

## Breaker Failure

One breaker fail element shall be available per each current input of the relay.

The breaker failure protection shall respond to three levels of current in three-pole and single-pole modes as well as to breaker contacts.

## End Fault Protection

One end fault protection element shall be available per each current input of the relay.

# Monitoring Functions

## CT Trouble

The element shall respond to differential current and when used in conjunction with voltage supervision or a check-zone shall provide desired response to CT fail conditions.

## Dynamic bus replica

The relay shall allow to associate a dynamic connection status signal with each input to the differential element in order to dynamically include or exclude a given current from the differential calculations.

The status signal could be any user flag available in the relay, especially position of any input contact or a combination of thereof via programmable logic.

The relay shall allow inverting any given current in software before configuring it for the bus differential zone. This allows easier application to bus couplers with single CTs.

## Isolator Monitoring

The relay shall provide for isolator monitoring functions responding to both normally open and normally closed auxiliary switches.

Isolator contact discrepancy alarm shall be incorporated. A provision of blocking switching operations in the substation, blocking selected protection functions and acknowledging the alarm shall be made.

The functional shall generate a reliable isolator position signal even during contact discrepancy situation.

# Control Functions

## Programmable logic including non-volatile latches

## Inputs/Outputs

- Flexible control of all input and output contacts shall be provided.

- All elements shall have a blocking input that allows supervision of the element from other elements, contact inputs, etc.

- The relay shall allow for peer-to-peer communications direct fiber or G.703 or RS422 interfaces.

## Switchable Setting Groups

The relay shall have switchable setting groups for dynamic reconfiguration of the protection elements due to changed conditions such as system configuration changes, or seasonal requirements.

# Metering and Monitoring Functions

## Currents and Voltages

- Voltage (phasors, symmetrical components), current (phasors, symmetrical components, true RMS values), and frequency.

- Differential and restraint currents shall be available in terms of magnitude and angle for easy testing, commissioning and troubleshooting.

## Trip Circuit Monitoring

UR Common Guideform Specifications

The relay shall be provided in one integrated package suitable for incorporation in an integrated substation control system. The relay shall be housed in a horizontal, 4 RU, 19-inch rack chassis configuration. It shall be a modular design to easily facilitate upgrading or repair by replacement of modules. The faceplate interface shall include an alphanumeric vacuum fluorescent display, keypad, and LED target indicators.

The logic that determines the interaction of inputs, features, and outputs shall be re-configurable through the use of FlexLogic™ equations. The use of remote inputs and outputs in addition to hardware shall be available on the communications ports using the UCA2 GOOSE (Generic Object Oriented Substation Event) mechanism to minimize the requirement for auxiliary components and wiring. The contact inputs shall accept wet or dry contacts. Contact outputs shall be trip rated Form-A with current and voltage circuit monitors, Form-C, or Fast Form-C for signaling. Hardware input/output capability shall be expandable.

The relay shall have three communications ports that operate independently and simultaneously. The RS232 port shall be accessible from the faceplate of the relay. The second port shall be RS485 supporting Modbus® RTU and DNP 3.0 protocols capable of baud rates up to 115 kbps. The third communications port shall be either a similar RS485 port or a 10 Mbps Ethernet port supporting MMS/UCA2, Modbus®/TCP, and DNP 3.0 or IEC 60870 protocols. The physical port shall be 10BaseF, or redundant 10BaseF.

The relay shall be supplied with supporting application software for use on a PC with Windows® 95/98/NT operating systems. The program shall be capable of retrieving Comtrade oscillography files from the relay to display, save, or print when troubleshooting. The software shall provide the capability of editing and managing settings files to store to the relay or disk backup, while on-line or off-line. The software shall also permit the updating of new relay firmware and viewing of all trip and alarm target messages, and the 1024 time stamped events recorded by the relay.

The relay clock shall be capable of being synchronized with an IRIG-B signal to allow synchronism with other connected devices. The relay shall allow for SNTP network-based time synchronization.