Guideform Specification

EPM5200 - Multifunction Electrical Power Monitor

PART  2       PRODUCTS

2.01Manufacturer

GE products have been used as the basis for design.  All Manufacturers’products shall be of equivalent quality, dimensions, with equivalent operating features and shall comply with all requirements specified or indicated in these contract documents.  Monitor shall be GE Model EPM5200.

2.02    	POWER METERS

A.	The Monitor shall be UL listed and CE marked and shall be rated for use at temperature from –25 degrees C to +70 degrees C.

B.	The Monitor shall accept input from standard instrument transformers (5A secondary current transformers and 120 volt secondary potential transformers). The monitor shall accept a voltage monitoring range of up to 600 volts, phase to phase.  The monitor shall have the following input handling characteristics:

- Shall withstand 200% rated current continuously. It shall withstand 10X rated current for at least 3 seconds.

- Shall be capable of connection to a three phase, four-wire wye system or a three phase, three wire, delta system.

- Surge withstand shall conform to IEEE C37.90.1

- Shall be user programmable to any PT or CT ratio. Programming data shall be password protected. DIP switches or other fixed ratio designs shall not be acceptable.

- PTs and CTs shall be physically connected on the secondary side.

- Voltage and current connections shall be segregated from each other on the back of the monitor to provide safe connections.

C.	The Monitor shall have an accuracy of +/- 0.3% or better for volts and amps, and 0.6% for power functions.

- The Monitor must measure true RMS voltage phase to neutral.

- The Monitor must measure true RMS voltage phase to phase.

- The Monitor must measure true RMS current per phase.

- The Monitor must measure true RMS neutral current.

- The Monitor must measure true RMS real power.

- The Monitor must measure true RMS reactive power.

- The Monitor must measure true RMS apparent power.

- The Monitor must measure power factor.

- The Monitor must measure frequency.

- The Monitor must be capable of providing readings for both instantaneous and average readings.

- The Monitor must also be capable of providing all single-phase real, apparent, reactive power and power factor values.

- The Monitor shall record and store total bi-directional energy. It shall include separate registers for positive and negative energy.

- The Monitor shall record and store total bi-directional accumulated energy and total accumulated apparent energy.

- The Monitor shall monitor max/min average demand values for all current and power readings. The demand interval shall be user programmable.

D.	The monitor shall include a three line, integrated, light-emitting diode (LED) display.

- The measured values must be displayed on 3 separate lines of LED’s.

- The Monitor must be capable of displaying one leg of volts, amps and total power simultaneously.

- The display shall provide user access to all phase voltages (phase to neutral and phase to phase), currents (phase and neutral), watts, VARs, VA, power factor, frequency and kwh

- The display must provide user access to max/min values for all displayed quantities.

E.	The monitor shall be microprocessor based and shall be fully user programmable.

- The Monitor must store 3 separate copies of the critical setup data in a write protected EEPROM. All 3 copies of the critical data must have independent checksums.

- The Monitor shall be configured through the front panel or through a computer interface. It shall not be necessary to dismantle the monitor to perform programming functions.

- Configuration data shall be password protected.

F.	Serial communications shall be provided via an RS232 or RS485 port.

- An RS232 or RS485 DB-9 Female port located on the back.

- The Monitor shall have a MODBUS RTU/ASCII and DNP 3.0 available as standard protocols.

- The Monitor shall have a communication baud rate of 9600 or higher.

- Capability of having up to 9999 separate addresses for multi-point communication.

- The digital port connections shall be separated from the voltage and current connections.

G.	The monitor case shall be fully enclosed and shielded.

- The Monitor shall fit a standard 4 1/2” switchboard instrument size mounting per ANSI C39.1. Any other mounting configuration shall be unacceptable.

- The Monitor shall have a separable input module that can be remote mounted up to 3 feet from the display mounting.

- The Monitor shall be rated for use at temperature from –20oC to +70oC.

H.	The Monitor shall support control power options for 120 VAC, 230 VAC, 125 volts AC/DC, or 24-48 VDC and shall be connected at the main equipment’s control power voltage.