F35 Guideform Specifications

Firmware revision 3.00

Feeder protection, control, monitoring and metering for up to 5 feeders with busbar voltage measurement or 6 feeders without busbar voltage shall be supplied in one integrated digital relay package for application on feeders and suitable for incorporation in an integrated substation control system.

# Protection Functions

## Overcurrent Protection

Time overcurrent elements: for phase, neutral and ground currents (two TOCs per CT bank, maximum 6) shall be provided.

Time overcurrent curve characteristics: IEEE, IEC, IAC, I2t, definite time and custom curve for precise or difficult coordination shall be provided.

Instantaneous over current elements: for phase, neutral and ground currents (two IOCs per CT bank, maximum 12) shall be provided.

## Sensitive Ground

The sensitive ground input shall be provided to detect ground fault on high impedance grounded systems.

## Voltage Protection

Two phase undervoltage elements shall be provided per each voltage input of the relay.

Auxiliary undervoltage and overvoltage elements shall be provided per each voltage input of the relay.

Neutral overvoltage element shall be provided per each voltage input of the relay.

## Frequency Protection

- Six underfrequency elements shall be available for load shedding.

# Control Functions:

## Automatic Recloser

- Four shot, three-pole single breaker autorecloser shall be provided.

- The autorecloser shall allow applying different dead-times for each shot.

## Programmable logic including non-volatile latches

## Eight FlexElements™ for user-definable protection functions

Flexible control of all input and output contacts shall be provided.

All elements shall have a blocking input that allows supervision of the element from other elements, contact inputs, etc.

The relay shall allow for peer-to-peer communications direct fiber or G.703 or RS422 interfaces.

## Switchable Setting Groups

- The relay shall have switchable setting groups for dynamic reconfiguration of the protection elements due to changed conditions such as system configuration changes, or seasonal requirements.

# Monitoring and Metering Functions:

## Metering functions

- Metering functions shall include voltage (phasors, true RMS values, symmetrical components), current (phasors, symmetrical components, true RMS values), real, reactive and apparent power, power factor, energy, demand and frequency.

## User-programmable oscillography

## User-programmable data logger

## Trip circuit monitoring

UR Common Guideform Specifications

Firmware revision 3.00

The relay shall be provided in one integrated package suitable for incorporation in an integrated substation control system. The relay shall be housed in a horizontal, 4 RU, 19-inch rack chassis configuration. It shall be a modular design to easily facilitate upgrading or repair by replacement of modules. The faceplate interface shall include an alphanumeric vacuum fluorescent display, keypad, and LED target indicators.

The logic that determines the interaction of inputs, features, and outputs shall be re-configurable through the use of FlexLogic™ equations. The use of remote inputs and outputs in addition to hardware shall be available on the communications ports using the UCA2 GOOSE (Generic Object Oriented Substation Event) mechanism to minimize the requirement for auxiliary components and wiring. The contact inputs shall accept wet or dry contacts. Contact outputs shall be trip rated Form-A with current and voltage circuit monitors, Form-C, or Fast Form-C for signaling. Hardware input/output capability shall be expandable.

The relay shall have three communications ports that operate independently and simultaneously. The RS232 port shall be accessible from the faceplate of the relay. The second port shall be RS485 supporting ModBus® RTU and DNP 3.0 protocols capable of baud rates up to 115 kbps. The third communications port shall be either a similar RS485 port or a 10 Mbps Ethernet port supporting MMS/UCA2, ModBus®/TCP, and DNP 3.0 or IEC 60870 protocols. The physical port shall be 10BaseF, or redundant 10BaseF.

The relay shall be supplied with supporting application software for use on a PC with Windows® 95/98/NT operating systems. The program shall be capable of retrieving Comtrade oscillography files from the relay to display, save, or print when troubleshooting. The software shall provide the capability of editing and managing settings files to store to the relay or disk backup, while on-line or off-line. The software shall also permit the updating of new relay firmware and viewing of all trip and alarm target messages, and the 1024 time stamped events recorded by the relay.

The relay clock shall be capable of being synchronized with an IRIG-B signal to allow synchronism with other connected devices. The relay shall allow for SNTP network-based time synchronization.