G60 Guideform Specifications

Firmware revision 3.00

The primary protection for the AC generator shall be an integrated digital relay package and suitable for incorporation into an integrated station control system.

# Protection functions:

## High Speed Generator Stator Differential

The differential element shall have a dual slope characteristic.

A directional check and saturation detection algorithm shall be included for enhanced performance during CT saturation.

## 100% Stator Ground

The element shall incorporate an adaptive algorithm that compares the third harmonic voltage measured at the neutral and the generator terminals.

## 3rd Harmonic Neutral Undervoltage

The element shall measure the third harmonic voltage at the generator neutral.

An adjustable power window shall supervise the element.

## Accidental Energization

The element shall consist of a definite time, overcurrent element.

Arming logic shall allow supervision by voltage and/or offline indication.

## Loss of Excitation

The element shall consist of two offset mho impedance zones.

Undervoltage supervision may be applied to either zone.

## Sensitive Directional Power

Two elements shall be included each consisting of two stages.

The element characteristic angle shall be adjustable.

## Generator Unbalance

The element shall respond to negative sequence current as a percentage of generator full-load current.

The element shall consist of an inverse time stage and a definite time stage.

The inverse time stage shall have an I2t characteristic with an adjustable definite minimum and maximum time.

The element shall have an adjustable linear reset characteristic.

## Overexcitation

Two elements shall be provided.

The element shall respond to the ratio of voltage over frequency.

Time overcurrent curve characteristics: Inverse A, Inverse B, Inverse C, definite time, and four custom curves for precise or difficult coordination shall be available.

The element shall have an adjustable linear reset characteristic.

## Abnormal Frequency

Six underfrequency and four overfrequency elements shall be provided.

## Backup Distance Protection

Individual measuring elements shall be provided for all phase loops.

Three zones of phase distance protection with memorized positive sequence voltage polarization, additional reactance, directional and overcurrent supervision shall be included.

Distance characteristics shall include mho, lens, and quadrilateral characteristics.

All zones shall have independent direction, shape, reach, maximum torque angle, overcurrent supervision, blinders and timer settings.

All phase distance zones shall work with CTs and VTs located independently from each other at any side of a three-phase wye-delta transformer. Accurate reach and targeting shall be provided regardless of zone direction and CT/VT location.

The distance elements shall include an adaptive reach feature for application on series compensated lines. The reach shall be adjusted automatically based on the current level to provide maximum security.

## Out-of-Step Protection and Power Swing Blocking

Integrated out-of-step tripping and power swing blocking functions shall be provided.

The out-of-step tripping protection shall be programmable to trip either in an early (instantaneous) or delayed (when the current envelope is at the minimum) mode.

Both out-of-step tripping and power swing blocking shall be programmable to work with 2 or 3 characteristics.

Current supervision shall be available for both the functions.

## Overcurrent Protection

One time overcurrent element for phase, neutral, and ground currents shall be provided. Voltage restraint shall be included.

Time overcurrent curve characteristics: IEEE, IEC, IAC, I2t, definite time, and four custom curves for precise or difficult coordination shall be available.

Six instantaneous overcurrent elements for phase currents shall be available.

One instantaneous overcurrent element for neutral and ground currents shall be available.

One phase directional overcurrent element shall be available.

Two neutral directional overcurrent elements shall be available.

## Voltage Protection

Two phase under- and one over-voltage elements shall be provided

Auxiliary under- and over-voltage elements shall be provided

A neutral overvoltage (3Vo) element shall be provided.

The voltage element operating time shall be user adjustable.

# Control Functions:

## Two Synchrocheck Elements

The synchrocheck elements shall be configurable to respond to any combination of single-phase voltages.

Dead source logic shall be included.

## Programmable logic including non-volatile latches

## Sixteen FlexElements™ for user-definable protection functions

Flexible control of all input and output contacts shall be provided.

All elements shall have a blocking input that allows supervision of the element from other elements, contact inputs, etc.

The relay shall allow for peer-to-peer communications direct fiber or G.703 or RS422 interfaces.

## Switchable Setting Groups

The relay shall have switchable setting groups for dynamic reconfiguration of the protection elements due to changed conditions such as system configuration changes, or seasonal requirements.

# Monitoring and Metering

## Monitoring Functions

- Voltage (phasors, true RMS values, symmetrical components), current (phasors, symmetrical components, true RMS values), real, reactive and apparent power, power factor, energy and frequency.

## User-programmable oscillography

## User-programmable Data Logger

## Trip circuit monitoring

UR Common Guideform Specifications

Firmware revision 3.00

The relay shall be provided in one integrated package suitable for incorporation in an integrated substation control system. The relay shall be housed in a horizontal, 4 RU, 19-inch rack chassis configuration. It shall be a modular design to easily facilitate upgrading or repair by replacement of modules. The faceplate interface shall include an alphanumeric vacuum fluorescent display, keypad, and LED target indicators.

The logic that determines the interaction of inputs, features, and outputs shall be re-configurable through the use of FlexLogic™ equations. The use of remote inputs and outputs in addition to hardware shall be available on the communications ports using the UCA2 GOOSE (Generic Object Oriented Substation Event) mechanism to minimize the requirement for auxiliary components and wiring. The contact inputs shall accept wet or dry contacts. Contact outputs shall be trip rated Form-A with current and voltage circuit monitors, Form-C, or Fast Form-C for signaling. Hardware input/output capability shall be expandable.

The relay shall have three communications ports that operate independently and simultaneously. The RS232 port shall be accessible from the faceplate of the relay. The second port shall be RS485 supporting ModBus® RTU and DNP 3.0 protocols capable of baud rates up to 115 kbps. The third communications port shall be either a similar RS485 port or a 10 Mbps Ethernet port supporting MMS/UCA2, ModBus®/TCP, and DNP 3.0 or IEC 60870 protocols. The physical port shall be 10BaseF, or redundant 10BaseF.

The relay shall be supplied with supporting application software for use on a PC with Windows® 95/98/NT operating systems. The program shall be capable of retrieving Comtrade oscillography files from the relay to display, save, or print when troubleshooting. The software shall provide the capability of editing and managing settings files to store to the relay or disk backup, while on-line or off-line. The software shall also permit the updating of new relay firmware and viewing of all trip and alarm target messages, and the 1024 time stamped events recorded by the relay.

The relay clock shall be capable of being synchronized with an IRIG-B signal to allow synchronism with other connected devices. The relay shall allow for SNTP network-based time synchronization.