Network Stability and Synchrophasor Measurement System

Guideform Specification

Network protection, control, monitoring, metering and synchrophasor measurements shall be supplied in one integrated system with up to 4 Phasor Measurement Units (PMU) packaged for application on the electrical network and suitable for incorporation in an integrated substation control system.

Applications shall include load shedding, remedial actions schemes and special protection schemes.

Protection Functions:

## I Network Protection

- The system shall have phase instantaneous overcurrent element with no intentional delay or with a definite time delay

- The system has 6 underfrequency elements that can be used in various load shedding and remedial action schemes

- The system has 4 overfrequency elements used to maintain power balance.  When the balance is disrupted the overfrequency element can used to restore the balance.

- Out-of-step tripping and power swing blocking measures the positive sequence apparent impedance and traces its locus with respect to either two or three operating characteristics boundaries. This element also incorporates an adaptive disturbances detector. This function is capable of detecting faster disturbances. MHO and Quad characteristics are supported.

- Open pole detection designed to detect if any pole associated with circuit breaker is opened or conductor is broken on the protected power line.

- The system shall have Synchrocheck function intended for supervising the paralleling of two parts of a system.

- The system shall have sensitive directional power function responds to three phase active power and is designed for reverse power and low forward power applications involving co-generations.

- The system shall have overvoltage element with no intentional delay or with a definite time delay. The input voltage is the phase-to-phase voltage, either measured directly from delta-connected VT or as calculated from phase to ground connected VTs.

- The system shall have undervoltage protection for voltage sensitive load. Voltage drop increases the drawn of current which may cause over heating. The undervoltage feature may be used to block external devices.

# II Control Functions:

## Programmable logic including non-volatile latches

Sixteen programmable element for user-definable protection functions

Flexible control of all input and output contacts shall be provided.

All elements shall have a blocking input that allows supervision of the element from other elements, contact inputs, etc.

The relay shall allow for peer-to-peer communications direct fiber or G.703 or RS422 interfaces.

Four programmable curves for custom curve development.

Programmable states -  Up to 256 logical variables under 16 modbus address

The system shall have 8 digital counters. Digital counter counts the number of state transition.

## VT Fuse Failure

The system shall have VT Fuse Failure detector function used to raise an alarm or to block that may operate incorrectly during VT fuse failure.

Frequency Rate of Change

Four independent rate of change of frequency elements are available.

Digitizer

Up to 5 digitizer elements shall be available. The digitizer used for peer to peer communications

## Switchable Setting Groups

The relay shall have 4 switchable setting groups for dynamic reconfiguration of the protection elements due to changed conditions such as system configuration changes, or seasonal requirements.

# III Inputs/Outputs

AC inputs (up to 8 3-phase AC inputs)

Contact Inputs (up to 96 inputs)

Virtual Inputs (64)

Contact outputs (up to 48 outputs)

Digital Outputs

Latching Outputs

Virtual Outputs (96)

Remote I/O - remote I/O provide a means of exchange digital and analog values using the IEC 61850 standard

Direct I/O

DCMA I/O

RTD Inputs

Transducer  I/O

# IV Monitoring and metering functions

- Local and Synchrophasor Voltage (phasors, true RMS values, symmetrical components), current (phasors, symmetrical components, true RMS values), real, reactive and apparent power, power factor and frequency.

## V Breaker Monitor

- Digital input modules include an active voltage monitor circuit connected across Form A contacts.

- The relay shall calculate an estimate of the per phase wear on the breaker contacts by measuring and integrating the current squared passing through the breaker contact as an arc.

## VI User-programmable oscillography (max 64 records)

- The system shall have oscillography waveform capture at set sampling rate as well as other relay data at the point of trigger. Trigger flags are programmable and multiple oscillography records can be captured simultaneously.

## VII User-programmable data logger

- The system shall have data logger samples and records up to 16 analog parameters at user defined sampling rate. This data can be downloaded using product PC software.

- The relay automatically partitions the available memory between channels in use.

## VIII Trip circuit monitoring

- Some versions of the digital input modules include an active voltage monitor circuit connected across the Form A contacts. The purpose of this is to continuously monitor and validate the status of the trip circuit.

Common Guideform Specification

The relay shall be provided in one integrated package suitable for incorporation in an integrated substation control system. The relay shall be housed in a horizontal, 4 RU, 19-inch rack chassis configuration. It shall be a modular design to easily facilitate upgrading or repair by replacement of modules. The faceplate interface shall include an alphanumeric vacuum fluorescent display, keypad, and 48 LED target indicators.

The logic that determines the interaction of inputs, features, and outputs shall be re-configurable through the use of programmable logic equations. The use of remote inputs and outputs in addition to hardware shall be available on the communications ports using the IEC61850 GOOSE (Generic Object Oriented Substation Event) mechanism to minimize the requirement for auxiliary components and wiring. The contact inputs shall accept wet or dry contacts. Contact outputs shall be trip rated Form-A with current and voltage circuit monitors, Form-C, or Fast Form-C for signaling. Hardware input/output capability shall be expandable.

The relay shall have three communications ports that operate independently and simultaneously. The RS232 port shall be accessible from the faceplate of the relay. The second port shall be RS485 supporting ModBus® RTU and DNP 3.0 protocols capable of baud rates up to 115 kbps. The third communications port shall be either a similar RS485 port or a 100/10 Mbps Ethernet port supporting Synchrophasor streaming, IEC 61850, ModBus®/TCP, and DNP 3.0 or IEC 60870 protocols. The physical port shall be 100/10BaseF, or redundant 100/10BaseF.

The relay shall be supplied with supporting application software for use on a PC with Windows® 98/NT/W2000/XP operating systems. The program shall be capable of retrieving Comtrade oscillography and synchrophasor files from the relay to display, save, or print when troubleshooting. The software shall provide the capability of editing and managing settings files to store to the relay or disk backup, while on-line or off-line. The software shall also permit the updating of new relay firmware and viewing of all trip and alarm target messages, and the 1024 time stamped events recorded by the relay.

The relay clock shall be capable of being synchronized with an IRIG-B signal to allow synchronism with other connected devices. The relay shall allow for SNTP network-based time synchronization.